Evant Ranch Water Collection Master Handoff

A thorough project-planning workbook for Luke

Prepared for Ben Peays | Ranch near Evant, Texas | 500 acres | June 21, 2026

## Purpose of this document

This packet is meant to let Luke take over the ranch water project without starting from zero. It captures the known facts, the first questions to answer, the design logic, the sizing math, the engineering risks, the regulatory items to verify, the contractor scopes, and a reusable prompt Luke can paste into his own chat to continue the work.

## Important limitation

This document is a planning and handoff workbook. It is not sealed engineering, legal advice, plumbing design, electrical design, hydrology certification, water-rights opinion, or a construction drawing set. A qualified rainwater designer, civil engineer, well contractor, plumber, electrician, and/or local regulatory authority should review the final design before spending significant money or constructing permanent infrastructure.

## Big idea

Do not treat this as merely a tank purchase. Treat it as a layered ranch water resilience project: clean roof water for storage and household/ranch backup, well-water protection and integration, and separate land-scale water management for the 500-acre ranch.

# 1. Luke: Ask These Questions Before Designing Anything

These are the first questions Luke should answer. The project should not move to tank purchase, trenching, foundation work, or pump selection until these answers are collected and organized. The fastest way to waste money is to design around assumptions instead of measurements.

| Category | Question Luke should answer | Why it matters |
| --- | --- | --- |
| Project mission | What is the primary goal: household backup, potable water, garden/irrigation, livestock, fire reserve, drought resilience, or whole-ranch hydrology? | Every design decision changes depending on the mission. |
| Project mission | Is this water intended to enter the house plumbing, or is it strictly non-potable ranch/irrigation water? | Potable use requires treatment, testing, backflow protection, and plumbing discipline. |
| Project mission | How many days of backup water does Ben want during drought, well failure, power outage, or pump failure? | Storage size should be tied to a real resilience goal. |
| Roof area | What is the actual horizontal roof catchment area in square feet, measured from roof plan/eaves, not guessed from house size? | 3,000 sq. ft. of living area may not equal 3,000 sq. ft. of collectable roof. |
| Roof area | Are there multiple roof planes? Which ones have gutters? Which can actually be routed to the same collection line? | Fragmented roof planes may require multiple downspout collection points. |
| Roof material | What is the roof material: metal, asphalt shingle, tile, membrane, coated metal, or something else? | Water quality, runoff efficiency, debris, treatment, and potable suitability change by material. |
| Gutters | What size are the existing gutters and downspouts? Are they clean, sloped correctly, and large enough for intense Texas storms? | The roof may generate water faster than small gutters can move it. |
| Downspouts | How many downspouts exist and where are they located? | This determines collection manifold design. |
| Conveyance | Does the proposed 100-yard pipe run go downhill, uphill, or through dips and rises from the house to the tank? | Gravity pipe, wet-line pipe, and pumped conveyance are different systems. |
| Conveyance | What is the vertical elevation difference from gutter outlet to tank inlet? | This determines whether water flows by gravity and whether pipe can drain. |
| Tank site | What is the exact proposed tank location, and why was that site chosen? | The tank site affects gravity flow, foundation, overflow, access, pump head, electrical cost, and visual impact. |
| Tank site | Can a truck deliver a large tank and base materials to the tank site in wet weather? | Access often drives cost and feasibility. |
| Foundation | What are the soils at the tank site: shallow rock, expansive clay, limestone, caliche, slope, fill, or erodible soil? | A full large tank can weigh hundreds of thousands of pounds. |
| Overflow | Where will tank overflow go during a major storm? | Overflow can erode the pad, flood structures, or create a nuisance if not planned. |
| Pump back uphill | How far and how high must water be pumped from tank to point of use? | Pump selection depends on total dynamic head and required gallons per minute. |
| Pump back uphill | What pressure and flow are required at the destination: house fixtures, hose bibs, irrigation zones, troughs, or fire hydrant? | A pump for a garden hose is not the same as a pump for household pressure or fire reserve. |
| Existing well | What is the well depth, static water level, pumping level, pump depth, casing size, pump horsepower, and tested yield? | The rainwater system should be designed with the well system, not in ignorance of it. |
| Existing well | Can Ben locate the driller log, pump installer record, water quality report, and any GCD registration/permit documents? | These documents are essential before deciding whether rainwater is supplement, backup, or primary. |
| Aquifer | Which aquifer and formation supply the well? | The area is likely related to Trinity aquifer units if in/near Coryell County, but this must be confirmed from well records. |
| Water quality | Has the well been tested recently for bacteria, nitrate, hardness, TDS, iron, manganese, arsenic, salinity, sulfate, and pH? | Treatment and plumbing choices depend on actual water chemistry. |
| Regulatory | Is the ranch in Coryell County, Hamilton County, or split across both? | This determines local groundwater district, county, and soil/water contacts. |
| Regulatory | If in Coryell County, has Middle Trinity GCD registration/permitting been reviewed? If in Hamilton County, has the correct jurisdiction been identified? | Do not assume one regulatory district without checking the parcel. |
| Surface water | Are there existing ponds, tanks, draws, creeks, dams, springs, low-water crossings, or drainage easements? | Land-scale runoff is regulated and engineered differently than roof rainwater. |
| Ranch use | How many livestock units, wildlife water points, gardens, orchards, food plots, pool, or landscaping zones need water? | Demand can dwarf roof yield. |
| Fire | Is one goal to have a fire reserve for structure protection, grassfire response, or volunteer fire department access? | Fire reserve changes tank size, outlet fittings, pad access, and dedicated storage volume. |
| Electrical | Is there power at the proposed tank site? If not, how far is the nearest service? | Electrical trenching and pump power may cost more than expected. |
| Backup power | Should the pump system work during power outages? | Generator interlock, solar, battery, or gravity-fed emergency connections may be needed. |
| Budget | What is the rough budget range: $25k, $50k, $100k, $250k+? | Scope must match budget reality. |
| Timeline | Is this needed this season, this year, or as a multi-year ranch master plan? | The order of work changes if there is urgency. |
| Aesthetics | Does Ben care about visibility of the tank, color, noise, fencing, screening, or impact on ranch-house view? | A large tank is a permanent visual object. |
| Maintenance | Who will clean filters, flush first-flush devices, check pumps, and test water? | A neglected rainwater system becomes unreliable quickly. |
| Operations | Does Ben want a simple manual system or an automated monitored system with tank sensor, pump controls, alerts, and freeze protection? | Controls and monitoring can prevent surprises. |
| Future expansion | Are there barns, sheds, carports, livestock shelters, or future structures that can add catchment area? | Additional roof area may matter more than a bigger tank. |

## Luke should make these three maps first

[ ] A roof-catchment map: roof planes, gutters, downspouts, pipe route, tank site, elevation arrows.

[ ] A water-use map: house, well, pressure tank, septic, garden, troughs, ponds, hydrants, roads, electrical, and proposed users of stored rainwater.

[ ] A ranch hydrology map: ridges, draws, existing ponds/tanks, roads, erosion points, low-water crossings, springs/seeps, creek channels, and candidate water-spreading or pond locations.

# 2. Paste-This-Into-ChatGPT Handoff Prompt for Luke

Luke can paste the following block into a new chat. It is written to give the next assistant the project context, the assumptions, the research standards, and the deliverables expected.

You are helping me manage a ranch water collection and water resilience project for a 500-acre ranch near Evant, Texas. The owner is Ben. I am Luke and I am taking over project coordination. Known facts and starting assumptions: - Ranch is approximately 500 acres near Evant, Texas. - Ranch has an existing ranch house, estimated around 3,000 square feet, with roofs and existing gutters. - Ben wants to collect rainwater from the roof, send it approximately 100 yards away to a storage tank, store it, and pump it uphill when needed. - Ben was considering an aluminum tank and did not initially plan a concrete base, but the foundation/base must be verified because large tanks are extremely heavy when full. - Existing well is on the property and may be deep; aquifer name, well depth, pump depth, static water level, pump yield, water quality, and regulatory records still need to be collected. - The system should be designed as a master plan, not just a tank purchase. - Roof rainwater, well water, and land-scale ranch runoff should be treated as related but distinct systems. - Potable vs non-potable use must be decided before final design. Critical known calculations to verify: - Rainwater harvesting formula: gallons = rainfall inches x roof catchment area sq. ft. x 0.623 x runoff coefficient. - Evant, Texas average annual precipitation is around 30.7 inches based on climate normal summaries, but use the best current local rainfall source and drought assumptions. - If collectable roof area is 3,000 sq. ft., then 1 inch of rain produces about 1,869 gallons before losses and roughly 1,400-1,680 gallons after real-world losses depending on efficiency. - At 30.7 inches/year and 3,000 sq. ft., the roof may yield roughly 43,000-52,000 gallons/year after losses. This is useful, but not huge by 500-acre ranch standards. - A 30,000-gallon tank weighs about 250,000 pounds full; a 50,000-gallon tank weighs about 417,000 pounds full; a 100,000-gallon tank weighs about 834,000 pounds full. Your job: 1. Ask me for missing data before making final recommendations. 2. Help me build a water audit, catchment model, demand model, tank-sizing model, conveyance plan, pump plan, treatment plan, regulatory checklist, and contractor scope. 3. Separate roof rainwater design from whole-ranch surface-water/pond/hydrology planning. 4. Keep design practical for a Texas ranch: durable, maintainable, freeze-aware, drought-aware, power-outage-aware, and contractor-friendly. 5. Tell me what I do not know, what can go wrong, what must be measured, and what requires professional review. 6. Do not assume the ranch is in Coryell County or Hamilton County until I provide parcel location; identify both possibilities and tell me how to confirm. 7. Use current Texas sources for regulatory, groundwater, rainfall, and technical information. Prioritize TCEQ, TWDB, Texas A&M AgriLife, Texas Well Owner Network, local groundwater districts, USDA NRCS, and the local Soil and Water Conservation District. First deliverables I need from you: - A list of exact measurements and documents I need to gather. - A one-page project charter. - A preliminary system architecture diagram in text form. - A preliminary calculation worksheet. - A decision tree for potable vs non-potable use. - A contractor walk-through checklist. - A bid scope template for tank, pad, pipe, pump, filtration, and electrical work.

# 3. Known Project Context and Working Assumptions

| Topic | Current understanding |
| --- | --- |
| Location | Ranch near Evant, Texas. Exact parcel/county should be verified. |
| Acreage | Approximately 500 acres. |
| Existing structure | Ranch house estimated around 3,000 sq. ft. with roofs and gutters. |
| Collection idea | Run roof rainwater approximately 100 yards to a storage tank. |
| Storage idea | Large above-ground tank; Ben mentioned aluminum and no concrete base as a possible direction. |
| Use idea | Store rainwater and pump it uphill when needed. |
| Existing water source | Existing well; likely deep, but well depth, aquifer, static level, yield, pump details, water quality, and registration/permitting are unknown. |
| Project need | A master plan and step-by-step process, not just an equipment list. |
| Major uncertainty | Potable vs non-potable use has not been decided. |
| Major warning | A 3,000 sq. ft. roof is a valuable but limited water source by 500-acre ranch standards. |

## The central design principle

Design this as a layered water system. Layer 1 is clean roof rainwater. Layer 2 is the existing well and household pressure system. Layer 3 is whole-ranch land and runoff management. These should be coordinated, but not carelessly mixed. Roof water can be managed to a higher water-quality standard. Surface runoff from roads, pastures, animal areas, or draws should not be mixed into potable or near-potable storage.

## The main early conclusion

A 3,000 sq. ft. roof in the Evant area may produce roughly 43,000 to 52,000 gallons in an average year after losses, but rainfall arrives unevenly and drought periods can be long. That means a 30,000 to 50,000 gallon tank may be realistic for the house roof. A 100,000+ gallon tank may make sense only if additional roofs or other reliable catchment areas are added, or if the tank is also filled from well water or delivered water.

## Decision points that should not be skipped

[ ] Final water use: potable, non-potable, irrigation, livestock, fire, or all of the above with separate plumbing zones.

[ ] Catchment area: actual measured roof area plus any additional roofs to be added later.

[ ] Tank location: selected by gravity, access, base, overflow, electrical, and pump head, not just convenience.

[ ] Tank type: selected by potable suitability, structural design, warranty, pad requirements, delivery, maintenance, and cost per gallon.

[ ] Well role: primary, backup, supplement, or emergency fill source.

[ ] Regulatory path: roof water, well water, surface water, ponds, dams, and plumbing all have different questions.

# 4. Project Architecture: Think in Three Separate Water Systems

Luke should resist the temptation to put every water idea into one tank. Water quality, ownership/regulation, treatment needs, and failure modes vary by source. Separate systems can still support each other through protected and controlled connections.

| Layer | Sources/components | Best uses | Design note |
| --- | --- | --- | --- |
| System A: Roof rainwater | House roof, gutters, downspouts, first flush, screened conveyance, clean tank | House backup, potable after treatment, garden, emergency reserve, possibly livestock | Relatively clean source; can be protected and treated. |
| System B: Existing well | Deep well, pump, pressure tank, controls, wellhead, aquifer | Existing domestic/ranch supply, backup fill, emergency support | May be the most reliable source but should be protected from overuse and contamination. |
| System C: Whole-ranch hydrology | Road runoff, draws, ponds, stock tanks, grass cover, terraces, swales, check dams, crossings | Livestock, wildlife, erosion control, recharge, drought resilience, fire water | Most important for 500 acres, but lower water quality and different legal/engineering issues. |

## Recommended conceptual flow for roof rainwater

Roof -> gutters -> leaf screens/downspout filters -> first-flush diversion -> conveyance pipe or wet-line system -> tank inlet screen/filter -> calm inlet -> storage tank -> floating intake -> pump/pressure controls -> treatment if potable -> isolated plumbing or dedicated non-potable distribution -> overflow to stable drainage area.

## Recommended conceptual flow for well integration

Existing well -> well pump -> pressure tank/controls -> existing domestic plumbing. If rainwater is connected to the house, the two sources should be separated by code-compliant backflow protection and a clear source-selection strategy. Do not connect rainwater, well water, and non-potable lines informally.

## Recommended conceptual flow for ranch-scale runoff

Ridges and roads -> slowed runoff -> spread water across pasture where possible -> stabilized draws/check structures -> properly designed ponds/stock tanks where appropriate -> protected spillways -> overflow paths that do not erode roads, tank pads, or neighboring property. This should be planned separately from clean roof-water storage.

# 5. Rainfall, Catchment, and Preliminary Water-Yield Math

The water math matters because tank size should be matched to both supply and demand. Storage does not create water; catchment area creates water. The tank only stores what the catchment can deliver.

## Core formula

A common rainwater harvesting formula is:

Gallons collected = rainfall inches x catchment area in square feet x 0.623 x runoff coefficient

Texas A&M AgriLife materials and calculators use this basic relationship and provide tools to evaluate whether storage and supplemental water are adequate over time. See sources [S2] and [S3].

## Evant-area annual rainfall assumption

For early planning, use approximately 30.7 inches/year as an Evant-area average annual precipitation figure, but Luke should replace this with the best parcel-specific climate normal and drought-model assumptions before final sizing. Source [S4] reports 30.71 inches average annual precipitation for Evant. Average rainfall is not a design guarantee; storage should be checked against dry months and drought years.

## Preliminary roof yield examples

| Scenario | Calculation | Approximate result |
| --- | --- | --- |
| 1 inch rain, 3,000 sq. ft. roof, no losses | 1 x 3,000 x 0.623 | 1,869 gallons |
| 1 inch rain, 3,000 sq. ft., 75% efficiency | 1,869 x 0.75 | 1,402 gallons |
| 1 inch rain, 3,000 sq. ft., 85% efficiency | 1,869 x 0.85 | 1,589 gallons |
| 1 inch rain, 3,000 sq. ft., 90% efficiency | 1,869 x 0.90 | 1,682 gallons |
| 30.71 inches/year, 3,000 sq. ft., 75% efficiency | 30.71 x 3,000 x 0.623 x 0.75 | 43,050 gallons/year approx. |
| 30.71 inches/year, 3,000 sq. ft., 85% efficiency | 30.71 x 3,000 x 0.623 x 0.85 | 48,790 gallons/year approx. |
| 30.71 inches/year, 3,000 sq. ft., 90% efficiency | 30.71 x 3,000 x 0.623 x 0.90 | 51,660 gallons/year approx. |

## Why average annual yield can mislead

- Rainfall is episodic. One intense storm can overflow an undersized tank while a long dry period can empty an oversized one.

- Tank sizing should be modeled month-by-month or day-by-day using rainfall records, demand, overflow, and starting tank level.

- A system that produces 49,000 gallons/year on average does not necessarily provide 134 gallons every day.

- The more critical the use, the more conservative the drought assumption should be.

- Irrigation demand usually occurs during the same hot/dry season when rainwater inflow is weakest.

## Catchment expansion logic

| Expansion idea | Why it may help | Design caution |
| --- | --- | --- |
| Add barn roof | Often more cost-effective than making one tank larger. | Measure every roof plane and determine whether water can gravity-flow or be pumped. |
| Add equipment shed/carport | Can be designed specifically as a rainwater catchment surface. | Metal roofs are often easier to keep clean and collect efficiently. |
| Add shade structures near garden/orchard | Combines shade, utility, and water collection. | May be useful if a garden or orchard is a major water demand. |
| Do not add dirty runoff to clean tank | Pasture/road runoff can carry manure, sediment, hydrocarbons, and pathogens. | Keep dirty runoff in ranch hydrology/pond systems, not potable/clean storage. |

# 6. Demand Model: Define What the Water Must Do

The next major task is estimating demand. A roof-water system can be very successful if the demand is disciplined. It can fail expectations if everyone imagines it will support all ranch uses without enough catchment.

## Demand categories Luke should quantify

| Demand | How to estimate | Design note |
| --- | --- | --- |
| House domestic | people x gallons/person/day x days | Decide whether rainwater will be used for all indoor fixtures or emergency backup only. |
| Drinking/cooking only | people x drinking/cooking gallons/day | This is a small demand and easier to make potable. |
| Toilets/laundry | fixture demand/day | Can use non-potable plumbing if designed correctly, but plumbing separation matters. |
| Garden/orchard | area x irrigation inches/week x season | Often the biggest roof-water demand. |
| Livestock | species x head count x gallons/head/day | Needs reliable trough design and freeze/float protection. |
| Wildlife | seasonal water points | May not need treated water; ranch-scale ponds may be better. |
| Fire reserve | dedicated gallons never used for routine demand | May require fittings and access for fire department or ranch equipment. |
| Equipment washing | gallons/use x uses/month | Can consume more water than expected. |
| Pool/hot tub | fill and top-off gallons | Usually not an ideal use for limited roof water unless planned. |
| Emergency reserve | minimum tank level | Set a low-level cutoff to preserve emergency water. |

## Demand worksheet

| Use | Unit demand | Frequency | Monthly demand | Notes |
| --- | --- | --- | --- | --- |
| Household drinking/cooking | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Household full domestic | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Guest house/cabin | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Garden | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Orchard | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Landscaping | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Livestock troughs | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Wildlife water | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Fire reserve | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Equipment wash | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |
| Other | ____ gallons/day or gallons/event | ____ days/month or events/month | ____ gallons/month | Notes: __________________ |

## Recommended design targets

[ ] Create a base-case demand model: what you expect to use in a normal year.

[ ] Create a drought-case demand model: what you will cut off first when rain does not come.

[ ] Create an emergency-case demand model: what water must be preserved if the well or power fails.

[ ] Create a future-case demand model: what changes if you add barns, cabins, garden expansion, livestock, or fire-protection goals.

# 7. Storage Tank Strategy

Tank size should be selected only after catchment, demand, drought assumptions, site constraints, and budget are understood. A bigger tank is not always a better system. A tank that is too small wastes stormwater to overflow; a tank that is too large may sit low and represent money tied up in unused capacity.

## Tank size reality check

| Tank volume | Approx. full water weight | Planning interpretation |
| --- | --- | --- |
| 10,000 gal | 83,400 lb water weight | Small backup/garden tank; easier logistics; not huge ranch resilience. |
| 20,000 gal | 166,800 lb water weight | Meaningful backup; may fit roof-only collection better if demand is modest. |
| 30,000 gal | 250,200 lb water weight | Likely serious roof-water system size to evaluate. |
| 50,000 gal | 417,000 lb water weight | Strong candidate if roof catchment is real and demand/reserve justify it. |
| 75,000 gal | 625,500 lb water weight | Likely needs additional catchment or well/delivery fill strategy. |
| 100,000 gal | 834,000 lb water weight | Very large for one 3,000 sq. ft. roof unless expansion or fire reserve justifies it. |

## Preliminary recommendation

With only the house roof and no other catchment, Luke should start by modeling 20,000, 30,000, and 50,000 gallon tanks. Do not jump to 100,000 gallons unless the model shows it is justified or the design adds barn/shed catchment, well-fill capability, delivered-water fill, or a dedicated fire reserve.

## Tank material comparison

| Tank type | Potential strengths | Cautions/questions |
| --- | --- | --- |
| Corrugated galvanized steel with liner | Common for large rainwater systems; scalable; replaceable liner; strong visual ranch fit. | Requires correct liner, roof, pad, penetrations, overflow, and warranty review. |
| Bolted steel tank | Robust and scalable; can be engineered for larger volumes. | Higher cost/installation complexity; foundation requirements may be significant. |
| Welded steel tank | Strong and durable when properly coated. | Usually more expensive; corrosion protection critical. |
| Polyethylene tank | Common, potable-rated options, easier at smaller sizes. | Very large volumes may require multiple tanks; UV and pad requirements matter. |
| Fiberglass tank | Durable, corrosion-resistant, can be potable-rated. | Cost/delivery/repair details must be evaluated. |
| Concrete tank/cistern | Massive, durable, thermal stability. | Higher construction complexity; cracking, sealing, and access matter. |
| Aluminum tank | Light relative to steel; corrosion-resistant in some conditions. | Not the default ranch rainwater choice; confirm potable rating, structural design, liner/coating, compatibility, warranty, and contractor experience. |

## Tank features checklist

[ ] Potable-water rating or suitable liner/coating if water may be used in the house.

[ ] Manufacturer-approved foundation detail.

[ ] Inlet screen or pre-filtration before water enters tank.

[ ] Calm inlet to reduce sediment disturbance.

[ ] Floating intake or outlet placed above sediment layer.

[ ] Lockable inspection hatch/manway.

[ ] Vent with insect screen.

[ ] Overflow sized at least as large as inflow and routed away from pad.

[ ] Drain/blowdown connection for maintenance.

[ ] Level indicator: simple sight gauge, ultrasonic sensor, pressure transducer, or app-connected monitor.

[ ] Low-water cutoff to protect pump and preserve emergency reserve.

[ ] Freeze protection for exposed valves and pipes.

[ ] Fencing or bollards if livestock, vehicles, or children have access.

[ ] Color/finish selected for heat, visibility, and ranch aesthetics.

# 8. Tank Pad, Foundation, and Site Work

The foundation is not a side issue. It is part of the tank. A full tank can weigh as much as a small building, and the load must remain level, supported, drained, and protected from erosion.

## Why "no concrete base" can still require engineering

A concrete slab is not always required, but a designed base is always required. A large tank base may be compacted select fill, crushed limestone, sand bedding, geotextile, a ring wall, concrete footing, or an engineered slab depending on tank type, soil, slope, and manufacturer requirements.

| Issue | Why it matters | What Luke should do |
| --- | --- | --- |
| Levelness | Large tanks tolerate very little uneven settlement. | Survey pad elevations before delivery; follow manufacturer tolerance. |
| Bearing capacity | Soils must support concentrated full-tank load. | Evaluate clay, shallow rock, fill, slope, and drainage. |
| Drainage | Water around pad can erode support and undermine tank. | Crown pad, daylight drains, route overflow, armor outlet. |
| Access | Delivery truck, crane, skid steer, gravel truck, and future maintenance need access. | Design road/turnaround before delivery day. |
| Overflow protection | A full tank overflowing during a storm can dump high flow next to the pad. | Pipe overflow to stable area with riprap or level spreader. |
| Erosion control | Tank site may concentrate runoff. | Use swales, berms, rock, vegetation, and spillway thinking. |
| Animal/vehicle protection | Livestock rubbing or vehicles backing into valves can damage system. | Use fencing, bollards, valve boxes, and protected manifolds. |

## Tank site scoring matrix

| Criterion | Candidate site A | Candidate site B | Notes |
| --- | --- | --- | --- |
| Gravity from roof to tank | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Pump head back to house | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Soil/foundation suitability | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Overflow route | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Electrical access | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Road/truck access | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Visibility/aesthetics | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Distance from septic/leach field | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Distance from trees/debris | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Future expansion room | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Freeze exposure | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |
| Security/fencing needs | Site A score 1-5: ____ | Site B score 1-5: ____ | Notes: ______________________________ |

## Do not approve site work until these are complete

[ ] Tank manufacturer foundation requirements have been obtained in writing.

[ ] Tank pad site has been located on a map and staked in the field.

[ ] Elevation difference from gutters to tank inlet is measured.

[ ] Elevation difference from tank outlet to destination is measured.

[ ] Overflow path is drawn and checked during/after rain if possible.

[ ] Base contractor confirms compaction method, materials, thickness, and drainage detail.

[ ] No septic components, underground utilities, or buried electrical are in the work area.

[ ] Access route for tank delivery is confirmed with the tank vendor.

# 9. Gutters, Downspouts, and 100-Yard Conveyance Line

The system begins at the roof. If gutters, downspouts, and conveyance cannot handle intense storms, the tank will not receive the water you think it will. Texas rainfall can arrive fast, so peak-flow capacity matters.

## Questions for the existing gutter system

[ ] Are gutters continuous and sloped correctly?

[ ] Are gutters undersized for roof area and local storm intensity?

[ ] Are there leaf guards? Do they shed heavy rainfall or block collection?

[ ] Can downspouts be enlarged or added?

[ ] Are downspouts currently connected to drain pipes or splash blocks?

[ ] Can every target downspout be routed to the same trunk line?

[ ] Will roof debris, pollen, acorns, asphalt granules, or bird droppings create maintenance problems?

[ ] Are there trees over the roof that increase debris load?

## Peak flow examples

| Rainfall intensity | Approximate flow formula | Approximate roof runoff |
| --- | --- | --- |
| 1 in/hour storm | 3,000 sq. ft. x 0.0104 x 1 | 31 gpm before losses |
| 2 in/hour storm | 3,000 sq. ft. x 0.0104 x 2 | 62 gpm before losses |
| 3 in/hour storm | 3,000 sq. ft. x 0.0104 x 3 | 94 gpm before losses |
| 4 in/hour storm | 3,000 sq. ft. x 0.0104 x 4 | 125 gpm before losses |
| 6 in/hour storm | 3,000 sq. ft. x 0.0104 x 6 | 187 gpm before losses |

These are rough planning examples, not final pipe design. Final conveyance sizing should consider roof layout, downspout count, rainfall intensity, pipe slope, friction, cleanouts, trapped water, sediment, and whether the pipe operates open-channel or pressurized/wet-line.

## Gravity line versus wet-line

| Conveyance type | Description | Advantages | Risks |
| --- | --- | --- | --- |
| Gravity-drained line | Pipe continuously slopes from roof collection to tank and drains after storm. | Simpler, less stagnant water, fewer freeze/mosquito issues. | Requires tank inlet lower than collection points and no dips. |
| Wet-line system | Pipe has low points and remains full between storms; water rises into tank when enough head exists. | Can collect from downspouts where continuous slope is hard. | Needs cleanouts, drains, mosquito control, freeze consideration, sediment management, and careful sealing. |
| Pumped conveyance to tank | Roof water collected in sump/basin and pumped to tank. | Can overcome elevation constraints. | Adds power dependence, pump maintenance, controls, and failure risk during storms. |

## Conveyance design checklist

[ ] Draw every downspout and trunk line.

[ ] Measure pipe route length, slope, and low spots.

[ ] Decide whether the pipe must be 4 inch, 6 inch, or larger based on peak flow and slope.

[ ] Install cleanouts at direction changes and low points.

[ ] Include screened inlet points and leaf/debris interception before buried pipe where practical.

[ ] Protect buried pipe from vehicle loads or install at correct depth/sleeving under roads.

[ ] Include drain valves or cleanout points for wet-line sections.

[ ] Avoid sharp bends and undersized fittings that reduce capacity.

[ ] Prevent mosquito entry with screens and sealed openings.

[ ] Plan freeze protection for exposed pipe, valves, and first-flush devices.

# 10. Debris Control, First Flush, and Tank Water Quality

Rainwater quality begins before the tank. The goal is to keep leaves, grit, insects, pollen, bird droppings, roof particles, and the dirtiest first roof wash out of storage whenever possible.

## Treatment before the tank

| Component | Purpose | Caution |
| --- | --- | --- |
| Gutter cleaning/leaf guards | Reduces bulk debris before downspouts. | Leaf guards can help or hurt depending on design and storm intensity. |
| Downspout screens | Catch leaves/acorns before buried pipe. | Must be accessible for cleaning. |
| First-flush diverter | Diverts first dirty roof wash away from tank. | Size and maintenance matter; stagnant diverter water can become a nuisance. |
| Tank inlet screen | Final defense against insects and debris entering tank. | Must handle peak flow without splashing or bypass. |
| Calm inlet | Introduces water low and gently so sediment is not stirred. | Useful for water clarity and intake quality. |
| Floating intake | Draws water below surface and above sediment. | Often better than drawing from tank bottom. |

## First-flush questions

[ ] How dirty is the roof after dry periods?

[ ] Are there overhanging trees, birds, squirrels, or heavy pollen?

[ ] Will the water be potable, near-potable, or only irrigation water?

[ ] Can the first-flush device drain automatically and be cleaned easily?

[ ] Where will first-flush water discharge without eroding or causing mud?

[ ] Should each downspout have a small diverter or should the trunk line have one larger diversion point?

## Tank water quality rules of thumb

- Keep sunlight, insects, animals, and organic debris out of the tank.

- Keep sediment accumulation low and provide a way to inspect/clean the tank.

- Do not place the tank where floodwater or dirty surface runoff can enter it.

- Never allow livestock to access or rub on potable/clean storage components.

- Do not use questionable roof coatings or materials for potable water without confirming suitability.

- For potable use, rely on actual lab testing and a defined treatment train, not appearance or taste.

# 11. Pumping Back Uphill: Pressure, Flow, and Controls

The pump design depends on total dynamic head, desired flow, desired pressure, pipe diameter, friction loss, elevation difference, and duty cycle. Do not size the pump by horsepower alone.

## Core pump math

Static elevation head: every 2.31 feet of vertical lift requires about 1 psi just to lift the water. This is before friction loss and before useful pressure at the destination.

Required pump pressure approx. = elevation lift psi + friction loss psi + desired pressure at use point

## Pump design data Luke must collect

[ ] Vertical rise from normal tank water level to highest point of use.

[ ] Horizontal pipe distance from tank to house/garden/trough/fire point.

[ ] Pipe material and intended pipe diameter.

[ ] Desired flow rate in gallons per minute for each use.

[ ] Desired pressure at fixture or manifold.

[ ] Whether the system will run one use at a time or multiple uses simultaneously.

[ ] Electrical power available: voltage, phase, amperage, distance to service.

[ ] Need for generator, battery, solar, or manual bypass during outages.

[ ] Control preference: manual switch, pressure switch/pressure tank, VFD constant pressure, float switches, app monitoring.

[ ] Low-level cutoff strategy to protect pump and preserve reserve water.

## Pump/control options

| Option | What it does | Best use | Caution |
| --- | --- | --- | --- |
| Simple transfer pump | Moving water from tank to a non-pressurized destination. | Simple irrigation, filling troughs, moving water. | Not ideal for household pressure. |
| Booster pump + pressure tank | Traditional pressure system. | House backup, hose bibs, modest irrigation. | Cycling and tank sizing matter. |
| Variable frequency drive pump | Maintains constant pressure by varying pump speed. | Household pressure and variable demand. | More electronics; needs protection and good installation. |
| Solar pump | Useful for troughs or remote storage. | Remote livestock/wildlife water. | Flow may be limited; storage and controls matter. |
| Fire/utility pump | High-flow pump for emergency use. | Fire reserve, high-volume transfer. | Separate design; may need dedicated outlet and power/fuel. |

## Distribution choices

| Destination | Design issue | When it makes sense |
| --- | --- | --- |
| Back to house | Requires backflow/source isolation and possibly treatment. | Best if household backup is the mission. |
| To garden/orchard manifold | Can be non-potable; pressure and filtration sized to irrigation. | Best if irrigation is the mission. |
| To livestock troughs | Use float valves, freeze protection, shutoff valves, and durable buried lines. | Best if ranch utility is the mission. |
| To fire point/hydrant | May require large outlet, dedicated reserve, road access, and fire department coordination. | Best if fire resilience is the mission. |
| To elevated header tank | Can create gravity pressure after pumping when power is available. | Useful for low-tech resilience if elevation works. |

# 12. Potable Versus Non-Potable Design

This is one of the most important project forks. A non-potable ranch water system can be relatively simple. A potable or household-integrated system requires disciplined treatment, testing, plumbing isolation, backflow protection, maintenance, and documentation.

## Decision tree

| Question | If yes | Design consequence |
| --- | --- | --- |
| Will people drink it, cook with it, brush teeth with it, or wash dishes with it? | Yes | Design as potable. Use treatment, testing, and plumbing/backflow review. |
| Will it supply showers, sinks, laundry, or toilets? | Yes | Decide whether potable or non-potable indoor use is allowed and permitted; plumbing separation matters. |
| Will it be used only for garden, hose bibs, troughs, trees, dust control, or equipment washing? | Yes | Non-potable may be appropriate; label lines and prevent cross-connection. |
| Will it connect to the existing well-fed house plumbing? | Yes | Require professional plumbing/backflow design. |
| Will it ever be used by guests or renters? | Yes | Be conservative; label and treat appropriately; document operation. |

## Potable treatment train concept

A typical potable rainwater treatment concept may include: protected roof catchment -> debris screening -> first flush -> clean storage -> sediment filtration -> carbon if needed -> fine filtration -> disinfection with UV and/or chlorination -> post-treatment monitoring and water testing. The exact treatment train depends on water quality, use, local code, and maintenance capacity. TCEQ notes that anyone using rainwater for drinking, cooking, or dishwashing should consider rainfall, collection area, storage, and treatment needed to make it safe. See source [S1].

## Non-potable design discipline

[ ] Label non-potable hose bibs and lines.

[ ] Avoid cross-connections with well or household potable plumbing.

[ ] Use backflow prevention where there is any connection risk.

[ ] Filter enough to protect pumps, valves, drip irrigation, and emitters.

[ ] Do not let non-potable systems look like drinking-water outlets for guests or children.

[ ] Keep system drawings and valve labels clear.

## Water testing plan

| Water source | When to test | Possible parameters |
| --- | --- | --- |
| Existing well | At least annually for bacteria and other core parameters; more often after flooding, well work, taste/odor changes, or illnesses. | Total coliform, E. coli, nitrate-nitrogen, salinity/TDS, arsenic, hardness, iron, manganese, sulfate, pH as appropriate. |
| Stored rainwater before potable use | Before first use and on a recurring schedule. | Bacteria, turbidity, pH, residual disinfectant if chlorinated, and any treatment-specific checks. |
| Post-treatment potable outlet | At commissioning and periodically. | Confirms the whole system is working, not just source water. |
| Irrigation water | When plant/soil issues arise. | Salinity, sodium, pH, alkalinity if used on sensitive plants or soils. |

Texas Well Owner Network resources emphasize that private well owners are responsible for water quality and provide education/testing resources; recent TWON events screen for contaminants such as total coliform bacteria, E. coli, nitrate-nitrogen, arsenic, and salinity. See sources [S12] and [S13].

# 13. Existing Well and Aquifer Integration

The existing well may be the most important part of the ranch water system. The rainwater project should reduce stress on the well, provide backup, and create flexibility, but it should not accidentally contaminate or complicate the well system.

## Well documents Luke should find

[ ] Well driller log or completion report.

[ ] Pump installation invoice or pump report.

[ ] Well depth, casing diameter, screened/open interval, pump depth, and static water level.

[ ] Pumping test, yield test, or gallons per minute estimate.

[ ] Pressure tank and controls information.

[ ] Electrical details: voltage, breaker size, pump horsepower.

[ ] Water quality test reports.

[ ] Well registration or operating permit records from the correct groundwater conservation district, if applicable.

[ ] Any well service history: pump replacements, low-water events, sand production, odor, bacteria, shock chlorination, repairs.

## Likely aquifer context, to be verified

The Evant/Coryell/Hamilton area may involve Trinity aquifer units, but Luke should not assume the exact aquifer or formation until he has the well log or official well record. TWDB describes the Trinity Aquifer as a major central and northeastern Texas aquifer composed of several smaller aquifers within the Trinity Group, including Glen Rose, Paluxy, Twin Mountains, Travis Peak, Hensell, and Hosston units. See source [S5].

If the ranch is in Coryell County, Middle Trinity Groundwater Conservation District is highly relevant. MTGCD states that its mission covers Bosque, Comanche, Coryell, and Erath Counties and involves conserving, preserving, and protecting groundwater resources. See sources [S6] and [S7]. If the ranch is in Hamilton County, Luke should verify the correct groundwater district or whether another local rule framework applies using TWDB/TAGD resources. See source [S8].

## Well role options

| Well/rainwater relationship | When it makes sense | Caution |
| --- | --- | --- |
| Well primary / rainwater backup | Least disruptive if well is strong and rainwater is for outages, garden, or reserve. | Keep systems separate or use controlled backup connection. |
| Rainwater primary / well backup | Possible for household use only if tank/catchment/treatment are strong enough. | Requires reliable treatment and enough storage/demand control. |
| Well fills tank when rain is low | Can create operational simplicity but uses groundwater to fill rain tank. | Need float controls, air gap/backflow, water quality, and groundwater rules. |
| Rainwater reduces well pumping for irrigation | Often a practical goal. | Use rainwater for garden/orchard first; preserve well for house/livestock. |
| Separate systems by use | Cleanest operational model. | House stays on well; rainwater serves garden/fire/troughs/backup. |

## Well protection checklist

[ ] Inspect wellhead for sanitary seal, casing height, drainage away from well, and damage.

[ ] Keep chemicals, fuel, manure, and fertilizers away from the wellhead.

[ ] Confirm septic location and setbacks relative to well and tank work.

[ ] Avoid trenching that disturbs well electrical or water lines.

[ ] Do not connect rainwater to well plumbing without backflow protection and professional review.

[ ] Track static water level periodically if possible.

[ ] Track pump run time or water use if adding high-demand uses.

[ ] Keep a well folder with all logs, tests, service records, and district correspondence.

# 14. Whole-Ranch Water Management for 500 Acres

The roof system is useful, but the 500-acre ranch itself is the bigger water opportunity. Whole-ranch water planning should aim to slow runoff, reduce erosion, improve infiltration, support livestock/wildlife, protect roads, and store water in the right places. This is a separate but complementary project.

## Do not mix clean roof water with dirty surface runoff

Surface runoff from roads, pastures, livestock areas, and draws can carry sediment, manure, pathogens, hydrocarbons, pesticides, and organic debris. It belongs in land-scale systems such as ponds, sediment basins, spreaders, or recharge-oriented structures, not in a clean roof-water tank intended for household or near-potable uses.

## Ranch water features to inventory

[ ] Existing ponds/stock tanks

[ ] Draws and creek channels

[ ] Ephemeral streams

[ ] Springs or seeps

[ ] Rocky outcrops

[ ] Eroded gullies

[ ] Road ditches and culverts

[ ] Low-water crossings

[ ] Water gaps/fences

[ ] Livestock loafing areas

[ ] Existing troughs

[ ] Old wells or abandoned wells

[ ] Septic systems

[ ] Fertilizer/chemical/fuel storage

[ ] Areas of heavy cedar/brush

[ ] Pasture condition and bare ground

[ ] Good dam sites

[ ] Overflow paths toward neighbors or county roads

## Land-scale water practices to evaluate

| Practice | Purpose | Caution |
| --- | --- | --- |
| Ponds / stock tanks | Store water for livestock, wildlife, fire, and aesthetics. | Needs watershed sizing, soils/geology, spillway, dam safety, and legal review. |
| Check dams / grade-control structures | Slow water in eroding draws and trap sediment. | Must be designed to pass floods without failure. |
| Road drainage improvements | Roads often concentrate erosive runoff. | Crown, water bars, rolling dips, culverts, and outlets matter. |
| Terraces / contour berms | Slow and spread runoff on slopes. | Need survey and soil suitability. |
| Swales / level spreaders | Spread water over vegetation instead of concentrating it. | Must not cause unintended saturation or erosion. |
| Brush management | Can improve grass cover and infiltration depending on context. | Needs land stewardship plan, not indiscriminate clearing. |
| Cross-fencing and water distribution | Moves grazing pressure and protects riparian/pond areas. | Requires trough plan and pipelines. |
| Riparian protection | Protects creeks/draws from erosion and contamination. | Fencing and managed access may be needed. |

## Local conservation resources

The Hamilton-Coryell Soil and Water Conservation District is the local SWCD listed by the Texas State Soil and Water Conservation Board, with contact information and meeting details available from TSSWCB. See source [S9]. TSSWCB identifies itself as the state lead agency for planning, management, and abatement of agricultural and silvicultural nonpoint-source water pollution. See source [S10]. USDA NRCS Web Soil Survey provides soil data for land-use decisions, but it warns that onsite investigation may still be needed for certain conservation and engineering applications. See sources [S11] and [S14].

## Ranch hydrology deliverables Luke should pursue

[ ] Aerial map with watershed boundaries and flow arrows.

[ ] Soils map from Web Soil Survey for the whole ranch and candidate pond/tank sites.

[ ] Existing pond inventory with approximate capacity, watershed, spillway condition, and sediment status.

[ ] Road drainage inventory showing where roads collect or dump water.

[ ] Erosion inventory with photos after storms.

[ ] Candidate projects ranked by benefit, cost, risk, and regulatory complexity.

[ ] Separate list of roof-water projects versus land-runoff projects.

# 15. Texas Regulatory and Legal Questions to Verify

Luke should verify local rules before construction. Roof rainwater collection is generally encouraged in Texas, but surface water, ponds, dams, groundwater wells, plumbing, electrical, septic setbacks, and public-water rules can raise separate issues. This section is a checklist, not a legal opinion.

## Roof rainwater

Texas Water Development Board notes statewide legal support for rainwater harvesting, including a Texas sales-tax exemption for rainwater harvesting equipment and restrictions on HOAs banning rainwater harvesting installations. See source [S3].

## Potable rainwater

TCEQ guidance asks key questions for rainwater intended for drinking, cooking, or washing dishes: how much rain falls, how much collection area is available, how much water can be stored, and what treatment will make it safe. See source [S1]. TCEQ public-water-system rules may not apply to a single private household in the same way they apply to public systems, but plumbing, treatment, testing, lender/insurance, rental/guest use, and local code issues still matter.

## Groundwater/wells

[ ] Confirm exact county and groundwater conservation district jurisdiction.

[ ] Find existing well registration/permit status.

[ ] Ask the correct GCD whether any new well, high-capacity pump, irrigation use, or commercial use changes requirements.

[ ] If in Coryell County, contact Middle Trinity GCD and review forms/rules.

[ ] If in Hamilton County or split across counties, confirm with TWDB/TAGD map/database and county records.

## Surface water, ponds, and impoundments

TCEQ states that anyone who wants to use surface water in Texas must first get permission from the state unless an exempt use applies; exemptions can include domestic and livestock use, wildlife management, and emergencies such as wildfires. See source [S15]. Texas A&M AgriLife/Texas water-law educational materials distinguish diffused surface water from state water and note exemptions for certain small ponds used for domestic, livestock, and wildlife purposes under capacity limits. See source [S16]. Luke should verify before building or modifying ponds, dams, diversions, or structures in watercourses.

## Regulatory call list

| Who to contact | Questions to ask | Notes |
| --- | --- | --- |
| Groundwater district | Confirm well registration, permit status, aquifer, rules for new wells/high-capacity pumps, and reporting. | Use parcel county first; MTGCD if Coryell. |
| County development/permitting office | Ask about plumbing, electrical, septic setbacks, floodplain, driveway/road crossing, large tank, and stormwater concerns. | May be county-specific. |
| TCEQ surface water/water rights | Ask before impounding or diverting surface water outside clear exemptions. | Especially for ponds/dams/creek work. |
| Local SWCD/NRCS | Ask about conservation plan, pond/site advice, erosion control, cost-share possibilities, soil reports. | Helpful for whole-ranch plan. |
| Licensed plumber | Backflow, household integration, non-potable labeling, potable treatment tie-in. | Critical if connected to house. |
| Licensed electrician | Pump service, controls, generator, grounding, trenching. | Do not improvise electrical at tank/pump. |
| Tank manufacturer | Foundation, warranty, potable liner, delivery, wind/seismic design, penetrations. | Must drive pad design. |

# 16. Project Phases and Deliverables

Luke should manage the project in phases. The purpose is to prevent premature purchases and force the project to move from assumptions to measured facts, then to a design, then to bids, then to construction.

| Phase | Main work | Deliverable |
| --- | --- | --- |
| Phase 0 - Project charter | Define mission, budget range, potable/non-potable intent, emergency goals, and decision authority. | 1-page charter and decision log. |
| Phase 1 - Data collection | Collect measurements, well records, maps, photos, elevations, water tests, rainfall assumptions, and regulatory contacts. | Data binder and site map. |
| Phase 2 - Water balance model | Model roof yield, demand, tank sizes, drought scenarios, and overflow. | Spreadsheet/model with 20k/30k/50k scenarios. |
| Phase 3 - Concept design | Choose system architecture, tank site, pipe route, pump strategy, treatment concept, and expansion plan. | Concept plan drawing and scope narrative. |
| Phase 4 - Professional review | Review with rainwater contractor, well contractor, plumber, electrician, and civil/site contractor as needed. | Marked-up concept and risk list. |
| Phase 5 - Budget and bids | Issue comparable bid scopes for tank, pad, trench/pipe, pump, treatment, electrical, controls, and ranch hydrology. | Bid comparison table. |
| Phase 6 - Construction | Build in correct sequence: pad/overflow, conveyance, tank, pump/electrical, treatment, connections, controls. | Construction log and as-built photos. |
| Phase 7 - Commissioning | Flush, test, disinfect if potable, verify pump pressure, check overflow, label valves, train owner. | Commissioning checklist and operating manual. |
| Phase 8 - Maintenance | Schedule filter cleaning, tank inspection, water testing, pump checks, freeze preparation, and storm inspections. | Annual maintenance calendar. |

## Decision log template

| # | Decision | Options considered | Final decision | Owner/date |
| --- | --- | --- | --- | --- |
| 1 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 2 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 3 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 4 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 5 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 6 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 7 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 8 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 9 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |
| 10 | Decision needed: __________________ | Options: __________________ | Decision: __________________ | Owner/date: __________ |

# 17. Data Collection Packet

This section is designed to become Luke’s first field workbook. Print it, take it to the ranch, and fill it out with measurements, photos, and notes.

## Roof measurement sheet

| Roof section | Length | Width/projection | Area | Notes |
| --- | --- | --- | --- | --- |
| Roof plane 1 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 2 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 3 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 4 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 5 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 6 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 7 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |
| Roof plane 8 | Length: ____ ft | Width/projection: ____ ft | Area: ____ sq. ft. | Gutter/downspout notes: __________________ |

## Downspout inventory

| ID | Roof area served | Size | Condition | Connect? | Photo |
| --- | --- | --- | --- | --- | --- |
| Downspout 1 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 2 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 3 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 4 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 5 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 6 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 7 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 8 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 9 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 10 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 11 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |
| Downspout 12 | Roof area served: ____ sq. ft. | Size: ____ | Condition: ____ | Can connect? Y/N | Photo #: ____ |

## Elevation survey sheet

| Point | Elevation | Method | Photo |
| --- | --- | --- | --- |
| Highest gutter outlet | ____ ft | How measured: laser level / survey / app / other | Photo #: ____ |
| Lowest gutter outlet | ____ ft | How measured: ____ | Photo #: ____ |
| Proposed trunk line high point | ____ ft | How measured: ____ | Photo #: ____ |
| Proposed trunk line low point | ____ ft | How measured: ____ | Photo #: ____ |
| Proposed tank pad grade | ____ ft | How measured: ____ | Photo #: ____ |
| Proposed tank inlet elevation | ____ ft | How measured: ____ | Photo #: ____ |
| House pressure system elevation | ____ ft | How measured: ____ | Photo #: ____ |
| Highest fixture/use point | ____ ft | How measured: ____ | Photo #: ____ |

## Tank site field notes

[ ] Stake tank center and estimated tank circumference.

[ ] Photograph site from north, south, east, west, and from ranch house view.

[ ] Walk overflow path downhill during dry weather and after rain if possible.

[ ] Check for soft soil, fill, rock ledges, animal burrows, tree roots, and erosion.

[ ] Confirm access route for delivery truck, base material trucks, skid steer, and future maintenance.

[ ] Mark underground utilities, septic, water lines, electrical, fiber, and gas/propane lines before digging.

[ ] Confirm whether livestock or vehicles can enter the tank area.

## Photo shot list

| Shot needed | Done | File names/notes |
| --- | --- | --- |
| Aerial/satellite screenshot with proposed tank site | [ ] | Photo numbers/files: ______________________________ |
| House all four sides | [ ] | Photo numbers/files: ______________________________ |
| Roof planes | [ ] | Photo numbers/files: ______________________________ |
| Each gutter run | [ ] | Photo numbers/files: ______________________________ |
| Each downspout | [ ] | Photo numbers/files: ______________________________ |
| Proposed pipe route every 50 ft | [ ] | Photo numbers/files: ______________________________ |
| Any road crossings | [ ] | Photo numbers/files: ______________________________ |
| Proposed tank site all directions | [ ] | Photo numbers/files: ______________________________ |
| Proposed overflow path | [ ] | Photo numbers/files: ______________________________ |
| Existing wellhead | [ ] | Photo numbers/files: ______________________________ |
| Pressure tank/control area | [ ] | Photo numbers/files: ______________________________ |
| Electrical panel nearest tank/pump | [ ] | Photo numbers/files: ______________________________ |
| Septic/cleanout area if known | [ ] | Photo numbers/files: ______________________________ |
| Existing ponds/tanks | [ ] | Photo numbers/files: ______________________________ |
| Erosion areas | [ ] | Photo numbers/files: ______________________________ |
| Road drainage/culverts | [ ] | Photo numbers/files: ______________________________ |
| Barns/sheds/future catchment roofs | [ ] | Photo numbers/files: ______________________________ |

# 18. Calculation Worksheets

Luke should build these calculations in a spreadsheet. Do not rely on one average annual number. The goal is to test tank performance across realistic rainfall and demand scenarios.

## Catchment worksheet

| Catchment | Area | Coefficient | Rainfall | Annual gallons |
| --- | --- | --- | --- | --- |
| Catchment 1 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 2 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 3 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 4 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 5 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 6 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 7 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 8 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 9 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |
| Catchment 10 | Area ____ sq. ft. | Runoff coefficient ____ | Annual rainfall ____ in. | Estimated annual gallons ____ |

## Tank scenario worksheet

| Tank size | Starting level | Overflow | Empty months | Supplement needed | Verdict |
| --- | --- | --- | --- | --- | --- |
| 10,000 gal | Starting level: ____ | Monthly overflow: ____ | Months empty: ____ | Supplement needed: ____ | Verdict: ____ |
| 20,000 gal | Starting level: ____ | Monthly overflow: ____ | Months empty: ____ | Supplement needed: ____ | Verdict: ____ |
| 30,000 gal | Starting level: ____ | Monthly overflow: ____ | Months empty: ____ | Supplement needed: ____ | Verdict: ____ |
| 50,000 gal | Starting level: ____ | Monthly overflow: ____ | Months empty: ____ | Supplement needed: ____ | Verdict: ____ |
| 75,000 gal | Starting level: ____ | Monthly overflow: ____ | Months empty: ____ | Supplement needed: ____ | Verdict: ____ |
| 100,000 gal | Starting level: ____ | Monthly overflow: ____ | Months empty: ____ | Supplement needed: ____ | Verdict: ____ |

## Pump head worksheet

| Input | Value | Notes |
| --- | --- | --- |
| Vertical rise from tank water level to use point | ____ ft | ____ psi = ft / 2.31 |
| Friction loss in pipe/fittings | ____ psi | Use pipe size/flow/friction table or pump designer. |
| Desired pressure at use point | ____ psi | Often 40-60 psi for house-like pressure; use actual target. |
| Safety/design margin | ____ psi | Add conservative margin. |
| Total required pump pressure | ____ psi | Elevation + friction + desired pressure + margin. |
| Desired flow | ____ gpm | Use largest simultaneous demand. |

## Water reserve policy worksheet

| Reserve category | Target | Rule |
| --- | --- | --- |
| Routine usable storage | ____ gallons | Above emergency reserve; available for normal use. |
| Emergency household reserve | ____ gallons | Cannot be used for irrigation. |
| Fire reserve | ____ gallons | Dedicated if fire goal is real. |
| Pump low-water cutoff | ____ gallons / ____ tank level | Set to protect pump/reserve. |
| Refill trigger | ____ gallons / ____ tank level | Action point to conserve, fill from well, or truck water. |

# 19. Contractor and Vendor Scope Templates

Luke should use scopes so bids are comparable. If contractors bid different assumptions, the cheapest number may not be the cheapest real project.

## Rainwater designer / system integrator scope

[ ] Visit ranch and review roof, gutters, tank site, elevation, existing well/pressure system, electrical, and intended uses.

[ ] Prepare preliminary catchment and demand model with at least three tank sizes.

[ ] Recommend tank type, size, location, and foundation requirements.

[ ] Size conveyance pipe and downspout collection system for peak storm flow.

[ ] Specify first-flush, screens, tank inlet, overflow, floating intake, pump, controls, and filtration/treatment.

[ ] Identify potable/non-potable separation and backflow needs.

[ ] Provide owner operating and maintenance plan.

[ ] Provide as-built sketch after installation.

## Tank vendor bid scope

[ ] Tank volume and dimensions.

[ ] Material, liner/coating, roof, color, warranty, and potable rating if applicable.

[ ] Required pad/foundation detail in writing.

[ ] Included fittings: inlet, outlet, overflow, drain, manway, vent, screens, level gauge.

[ ] Delivery requirements, crane/assembly requirements, truck access needs.

[ ] Wind/structural design assumptions.

[ ] Installation timeline and owner responsibilities.

[ ] Exclusions and change-order rates.

## Pad/site contractor bid scope

[ ] Clear and prepare tank site according to tank manufacturer requirements.

[ ] Excavate/grade, install geotextile if specified, place compacted select fill/crushed limestone/sand bedding as required.

[ ] Confirm levelness and compaction method.

[ ] Install drainage around pad and stable overflow path with erosion protection.

[ ] Protect from vehicle/livestock damage as specified.

[ ] Provide photos during each layer of base construction.

[ ] Coordinate final inspection before tank delivery.

## Trenching/pipe contractor bid scope

[ ] Install roof-to-tank conveyance pipe sized per design.

[ ] Include downspout tie-ins, cleanouts, drains, inspection ports, and road-crossing sleeves as required.

[ ] Maintain proper slope or wet-line design as specified.

[ ] Bed and backfill pipe to protect from crushing and settling.

[ ] Mark pipe route and provide as-built measurements/photos before backfill.

[ ] Restore disturbed areas and prevent erosion.

## Pump/electrical bid scope

[ ] Install pump sized for required total dynamic head and flow.

[ ] Install pressure tank/VFD/control system as specified.

[ ] Install low-water cutoff, float switches/sensors, pressure gauges, isolation valves, unions, check valves, and bypasses as required.

[ ] Run electrical service to code, including disconnects, grounding, conduit, trench depth, and GFCI/surge protection where appropriate.

[ ] Coordinate generator or backup-power compatibility if required.

[ ] Demonstrate pump operation at design flow/pressure before final payment.

## Plumber/treatment bid scope

[ ] Confirm potable versus non-potable intended use.

[ ] Design and install filtration/disinfection if potable or near-potable.

[ ] Provide backflow protection/source isolation between rainwater and well/house systems.

[ ] Label non-potable lines and fixtures.

[ ] Provide sampling ports before and after treatment.

[ ] Provide filter replacement schedule and owner training.

[ ] Provide as-built plumbing diagram.

## Bid comparison table

| Scope item | Bid A | Bid B | Bid C | Notes |
| --- | --- | --- | --- | --- |
| Tank | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Pad/base | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Conveyance pipe | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Pump/controls | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Electrical | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Filtration/treatment | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Plumbing/backflow | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Overflow/erosion | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Monitoring/sensors | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |
| Other | Vendor A $____ | Vendor B $____ | Vendor C $____ | Notes/differences: __________________ |

# 20. Recommended Construction Sequence

The sequence matters. If you trench first and then change the tank site, money is wasted. If you install the tank before the overflow and pad are right, the system is vulnerable. If you connect plumbing before water quality is tested, you create risk.

| Step | Action |
| --- | --- |
| 1 | Finalize project charter and intended water uses. |
| 2 | Collect data: roof, elevations, well records, water tests, maps, photos. |
| 3 | Choose potable/non-potable architecture. |
| 4 | Model tank sizes and demand scenarios. |
| 5 | Select tank site after scoring gravity, pump head, access, foundation, overflow, and aesthetics. |
| 6 | Obtain tank manufacturer foundation requirements. |
| 7 | Confirm regulatory/plumbing/electrical/well questions. |
| 8 | Bid tank, pad, pipe, pump, treatment, and electrical scopes. |
| 9 | Stake tank site, pipe route, electrical route, overflow route. |
| 10 | Call utility locate and verify septic/well lines. |
| 11 | Build pad/foundation and overflow drainage first. |
| 12 | Install conveyance trench/pipe, downspout collection, cleanouts, first flush, and inlet protection. |
| 13 | Install tank and fittings. |
| 14 | Install pump, controls, electrical, filtration/treatment, and plumbing/backflow. |
| 15 | Flush, pressure test, leak test, verify overflow, and test pump flow/pressure. |
| 16 | If potable, disinfect/treat and lab test before use. |
| 17 | Label valves/lines, create as-built diagram, and train owner/operator. |
| 18 | Set maintenance calendar and spare parts list. |

## Commissioning checklist

[ ] Every downspout flows where expected during hose test or first storm.

[ ] No gutter overflow at ordinary rain intensity; note any overflow points in heavy storms.

[ ] First-flush diverters fill and drain as intended.

[ ] Tank inlet screen handles flow and does not splash excessively.

[ ] Tank overflow discharges away from pad without erosion.

[ ] Pump primes reliably and shuts off correctly.

[ ] Pressure at use point meets design target.

[ ] Low-water cutoff works.

[ ] Backflow/source isolation verified by plumber if connected to house/well plumbing.

[ ] Electrical disconnects, breakers, and controls are labeled.

[ ] All non-potable outlets are labeled.

[ ] Owner has spare filters, o-rings, pressure gauges, and vendor contact list.

[ ] As-built photos and drawings are stored digitally.

# 21. Operations and Maintenance Plan

A rainwater system is not set-and-forget. Maintenance should be simple enough that the ranch actually does it. Design choices should reduce maintenance burden, but not pretend it disappears.

| Frequency | Tasks | Notes |
| --- | --- | --- |
| After major storm | Check gutters, downspout screens, first flush, tank inlet, overflow, erosion, and pad drainage. | Especially important during first season. |
| Monthly during rainy season | Inspect debris screens, first flush drains, tank level, pump area, and leaks. | Clean as needed. |
| Quarterly | Inspect tank exterior, pad settlement, valves, gauges, filters, electrical controls, and rodent/insect entry points. | Document with photos. |
| Before freeze season | Insulate/protect exposed pipe, drain vulnerable lines, test heat tape if any, verify power backup. | Central Texas freezes can damage exposed water systems. |
| Annually | Clean gutters, inspect tank interior if safe/appropriate, test well water, test potable rainwater if used, review pump performance. | Schedule before peak demand season. |
| Every 3-5 years or as needed | Sediment inspection/cleaning, pump service, liner inspection, control upgrades. | Depends on debris and use. |

## Spare parts list

[ ] Replacement filter cartridges and housings o-rings.

[ ] Spare screen mesh for inlet/downspout filters.

[ ] PVC fittings, unions, valves, pipe repair couplings, primer/cement if system uses PVC.

[ ] Pressure gauge.

[ ] Pump control fuses or components recommended by installer.

[ ] Float switch if used.

[ ] Hose fittings and adapters.

[ ] Water test kit supplies or lab sample bottles if applicable.

[ ] Labels/tags for valves and non-potable outlets.

## Operating rules

- Set a minimum reserve level that routine irrigation cannot use.

- Log tank level monthly for the first year.

- Log pump run times/failures and unusual noises.

- After a long dry spell, expect first rain to be dirtier and check first-flush function.

- Do not bypass filters/disinfection for potable use.

- Do not let contractors connect temporary lines that defeat backflow protection.

- Keep a printed as-built diagram near the pressure/pump controls.

# 22. Risk Register: What Can Go Wrong

This project has several common failure modes. The point of a risk register is not to be pessimistic; it is to spend money once instead of twice.

| Risk | Consequence | Mitigation |
| --- | --- | --- |
| Oversized tank, undersized roof | Tank often low; money tied up in capacity that rarely fills. | Model catchment and demand before tank purchase. |
| Undersized gutters/downspouts | Water spills off roof instead of reaching tank. | Evaluate peak storm flow; add/enlarge downspouts. |
| Bad tank foundation | Settlement, tank damage, leaks, warranty denial. | Follow manufacturer base requirements; verify soils/drainage. |
| Poor overflow routing | Pad erosion, flooding, road damage. | Design stable overflow path before tank install. |
| Wrong pump | Low pressure, pump cycling, burned pump, high energy use. | Size for total dynamic head and actual demand. |
| Cross-connection | Contamination of potable/well water. | Use plumber and backflow/source isolation. |
| Untreated potable use | Health risk. | Design treatment and test water. |
| Dirty runoff in clean tank | Sediment/pathogens/maintenance nightmare. | Keep roof water separate from surface runoff. |
| Wet-line stagnation | Odor, mosquitoes, sediment, freeze damage. | Design cleanouts, drains, screens, and maintenance access. |
| Electrical shortcuts | Shock/fire/equipment damage. | Use licensed electrician and code-compliant installation. |
| Freeze damage | Broken valves/pipes/pump components. | Protect exposed components and plan winterization. |
| No maintenance owner | System gradually fails. | Assign maintenance tasks and schedule. |
| Regulatory surprise | Delay, fines, redesign. | Call GCD/county/TCEQ/SWCD early. |
| Pond/dam failure | Property damage, downstream impacts. | Use NRCS/civil engineer for land-scale impoundments. |

## Red flags requiring professional review

[ ] Any connection between rainwater and household potable plumbing.

[ ] Any connection between rainwater system and well system.

[ ] Any large tank on slope, fill, expansive clay, or questionable soil.

[ ] Any dam, pond, diversion, or work in/near a defined channel or creek.

[ ] Any high-flow fire water outlet or claim of fire protection.

[ ] Any electrical work beyond plug-in temporary equipment.

[ ] Any system that will be used by guests, renters, workers, or public users.

[ ] Any roof material or coating not clearly suitable for intended water use.

# 23. Budget Framework

Costs vary widely by tank size, tank material, site conditions, trenching, electrical distance, pump complexity, treatment, and whether professional design is needed. This section does not guess current prices; it organizes cost categories so Luke can get comparable bids.

| Category | Includes | Budget |
| --- | --- | --- |
| Design/consulting | Rainwater designer, civil/site engineer, plumber, electrician, well contractor, SWCD/NRCS assistance if applicable. | $____ |
| Tank | Tank shell, liner/coating, roof, fittings, delivery, installation, warranty. | $____ |
| Pad/foundation | Clearing, excavation, fill, crushed stone, sand, compaction, drainage, erosion protection, access road. | $____ |
| Gutters/downspouts | Cleaning, resizing, added downspouts, screens, leaf guards, collection boxes. | $____ |
| Conveyance pipe | Pipe, fittings, trenching, bedding, cleanouts, drains, road crossings, backfill/restoration. | $____ |
| First flush/pre-filtration | Diverters, screens, tanks/standpipes, automatic drains, inlet strainers. | $____ |
| Pump/controls | Pump, pressure tank or VFD, gauges, valves, float switches, sensors, low-water cutoff. | $____ |
| Electrical | Trench, conduit, wire, panel, disconnect, controls, generator provisions, surge protection. | $____ |
| Treatment | Sediment filtration, carbon, UV, chlorination, lab testing, sample ports, bypasses. | $____ |
| Plumbing/backflow | House connection, isolation valves, backflow prevention, labeling, non-potable plumbing. | $____ |
| Monitoring | Tank level sensor, flow meter, pressure sensors, alerts, data logging. | $____ |
| Fencing/protection | Fence, bollards, valve boxes, insulation, freeze protection. | $____ |
| Ranch hydrology | Soil survey, pond design, road drainage, check dams, erosion work, NRCS/civil review. | $____ |
| Contingency | Unknowns, rock trenching, change orders, material escalation. | $____ |

## Budget discipline

- Separate must-have from nice-to-have.

- Do not compare bids unless they include the same assumptions and exclusions.

- Require written foundation requirements before pad bid.

- Require as-built photos before trench backfill.

- Hold final payment until commissioning checklist is complete.

- Keep 15-25% contingency for trenching, rock, electrical, and site surprises.

# 24. Luke’s Project Management Workflow

Luke’s job is to turn Ben’s vision into a measured, documented project. The project should have one source of truth: a folder with maps, records, calculations, bids, decisions, photos, and final as-builts.

## Suggested folder structure

Evant Ranch Water Project/ 01_Project_Charter/ 02_Maps_and_Aerials/ 03_Roof_and_Gutter_Measurements/ 04_Well_Records_and_Water_Tests/ 05_Rainfall_and_Water_Balance_Model/ 06_Tank_Site_and_Elevation_Survey/ 07_Regulatory_and_Contacts/ 08_Design_Concepts/ 09_Bids_and_Budgets/ 10_Construction_Photos/ 11_Commissioning_and_Testing/ 12_As_Builts_and_Maintenance/

## Weekly project update template

Subject: Evant Ranch Water Project - Weekly Update 1. What we learned this week: - 2. Decisions needed from Ben: - 3. Measurements/documents still missing: - 4. Contractor/vendor activity: - 5. Risks or red flags: - 6. Next actions before spending money: -

## One-page project charter template

| Item | Answer |
| --- | --- |
| Project name | Evant Ranch Water Collection and Water Resilience Project |
| Owner | Ben Peays |
| Project coordinator | Luke |
| Primary goal | ____________________________________________ |
| Secondary goals | ____________________________________________ |
| Potable or non-potable? | ____________________________________________ |
| Initial catchment | Ranch house roof; actual measured area: ____ sq. ft. |
| Additional catchment | Barns/sheds/future roofs: __________________ |
| Tank scenario to model | 20k / 30k / 50k / other: __________________ |
| Existing well role | Primary / backup / fill source / separate: __________________ |
| Budget range | ____________________________________________ |
| Timeline | ____________________________________________ |
| Non-negotiables | Safety, water quality, foundation, overflow, backflow, maintainability. |

# 25. Exhaustive Question Bank for Luke

The following question bank is intentionally long. Luke does not need every answer on day one, but every answer will either shape design, reduce risk, or help contractors bid accurately.

## Owner goals

[ ] What problem is this project trying to solve first?

[ ] What would make the project a success one year after installation?

[ ] What water uses are absolutely not allowed to run dry?

[ ] How much inconvenience is acceptable during drought?

[ ] Does Ben want a showpiece system or a hidden utility system?

[ ] What level of automation does Ben want?

[ ] How much maintenance is acceptable?

[ ] Who will be responsible for maintenance when Ben is not present?

[ ] Does the system need to serve future cabins, barns, or livestock expansion?

[ ] Should the system increase property value, operational resilience, or both?

## Roof and gutters

[ ] What is the actual roof footprint?

[ ] What roof planes can be connected?

[ ] Are there roof valleys that concentrate flow?

[ ] What material is the roof?

[ ] How old is the roof?

[ ] Are there coatings, sealants, moss treatments, or chemical residues?

[ ] Are gutters properly sloped?

[ ] Are gutters seamless or sectional?

[ ] Are downspouts too few or too small?

[ ] Where does current roof water discharge?

[ ] Does roof water currently cause erosion near the house?

[ ] Would gutter modifications affect appearance?

[ ] Can gutter work be done without damaging fascia/roofing?

[ ] Are trees contributing leaves/acorns?

[ ] Does the roof collect ash, dust, or animal droppings?

## Tank site

[ ] Why was this site chosen?

[ ] Is it lower than the roof?

[ ] Is it lower or higher than the house?

[ ] How far from the house?

[ ] How far from power?

[ ] Can it be hidden from main views?

[ ] Is it accessible by truck?

[ ] Is it on natural ground or fill?

[ ] Does water flow toward or away from it during storms?

[ ] Is it near trees whose roots could affect base?

[ ] Is it near livestock?

[ ] Is it near septic or well?

[ ] Can overflow go somewhere safe?

[ ] Is there room for a second tank later?

[ ] Will the tank shade or affect anything nearby?

## Pipe route

[ ] What is the exact route from house to tank?

[ ] Does it cross roads, driveways, utilities, fences, or rocky areas?

[ ] Will trenching hit rock?

[ ] Can pipe maintain slope?

[ ] Are cleanouts accessible?

[ ] Can future leaks be located?

[ ] Will pipe be deep enough for protection?

[ ] Are there low points that hold water?

[ ] Is there a way to drain the pipe?

[ ] Will the pipe route conflict with future landscaping or roads?

## Pump/distribution

[ ] What is the vertical lift?

[ ] What is the desired flow?

[ ] What is the desired pressure?

[ ] Will the pump feed the house, a hose, irrigation, troughs, or fire equipment?

[ ] Will multiple uses run at once?

[ ] Will the pump be noisy near living areas?

[ ] Is power reliable?

[ ] Will generator backup be installed?

[ ] What happens if the pump fails?

[ ] Can the pump be isolated and serviced?

[ ] Is there a bypass?

[ ] Is there a dry-run cutoff?

[ ] Can the system be winterized?

## Water quality

[ ] Will anyone drink this water?

[ ] Will guests use it?

[ ] Will it touch dishes or cooking surfaces?

[ ] Will it be used in showers?

[ ] Will it be used for pets or livestock?

[ ] What roof contaminants are possible?

[ ] How often will filters be changed?

[ ] Who will test water?

[ ] What lab will be used?

[ ] What is the target water quality standard?

[ ] How will non-potable outlets be labeled?

[ ] Can there be any cross-connection with well water?

## Well/aquifer

[ ] What is the well depth?

[ ] What is the static water level?

[ ] What is the pumping level?

[ ] What is the pump depth?

[ ] What is the pump horsepower?

[ ] What is the tested yield?

[ ] Has the well ever run low?

[ ] Does the well produce sand?

[ ] Does the water smell, stain, or taste salty/hard?

[ ] What aquifer/formation is listed on the log?

[ ] Is the well registered?

[ ] What GCD rules apply?

[ ] Could rainwater reduce well pumping during dry months?

[ ] Should the well be able to fill the tank through an air gap?

## Ranch hydrology

[ ] Where does water enter the ranch?

[ ] Where does water leave the ranch?

[ ] Where are the main divides/ridges?

[ ] Which roads concentrate runoff?

[ ] Which gullies are actively eroding?

[ ] Which ponds hold water longest?

[ ] Which ponds leak or silt up?

[ ] Where would water storage help grazing distribution?

[ ] Where would a pond create regulatory or dam-safety issues?

[ ] Where can runoff be spread instead of impounded?

[ ] What areas need vegetation recovery?

[ ] Are there springs or seeps worth protecting?

## Regulation/insurance

[ ] What county is the tank in?

[ ] What GCD applies?

[ ] Does any county permit apply to large tank, plumbing, electrical, floodplain, septic, or road crossing?

[ ] Will there be any surface-water diversion or impoundment?

[ ] Are any dams large enough to trigger review?

[ ] Does homeowner/ranch insurance care about large tanks or fire-water claims?

[ ] Could guest/rental use change water system obligations?

[ ] Do contracts need indemnity, insurance, and warranty language?

# 26. Three Possible Project Scopes

Luke should present Ben with scope options so the project does not balloon without decisions. These are conceptual packages, not final quotes.

| Scope | Includes | Strength | Caution |
| --- | --- | --- | --- |
| Scope 1: Practical roof-water backup | 20k-30k tank, clean roof collection, non-potable garden/ranch use, pump to hose/garden, no house plumbing tie-in. | Lower complexity, faster, safer first phase. | Does not fully solve household potable backup. |
| Scope 2: Serious household/ranch backup | 30k-50k tank, stronger conveyance, pump/pressure controls, treatment-ready, possible protected house tie-in, monitoring. | Balanced resilience and usability. | Requires plumber/backflow/treatment review. |
| Scope 3: Ranch water master plan | Roof system plus barn catchment, fire reserve, well integration, ponds, road drainage, erosion control, NRCS/SWCD involvement. | Best long-term 500-acre strategy. | Multi-phase, higher cost, needs professional planning. |

## Recommended path

Start with Scope 2 as the planning target and Scope 3 as the long-term ranch framework. Scope 1 may be a good first construction phase if Ben wants to move faster and avoid household tie-in until water quality and plumbing issues are fully resolved.

# 27. Source List for Luke

Use these as starting references. Luke should verify current rules and site-specific facts before final design. These sources are included as plain URLs so they can be copied into a browser or a future chat.

| ID | Source | URL | Use |
| --- | --- | --- | --- |
| [S1] | TCEQ - Rainwater Collection and Treatment | https://www.tceq.texas.gov/drinkingwater/rainwater.html | Questions for rainwater used for drinking/cooking/dishwashing. |
| [S2] | Texas A&M AgriLife - Rainwater Harvesting Calculators | https://rainwaterharvesting.tamu.edu/calculators/ | Storage modeling and supplemental water concepts. |
| [S3] | TWDB - Rainwater Harvesting | https://www.twdb.texas.gov/innovativewater/rainwater/ | Texas rainwater harvesting information, tax exemption and HOA protections. |
| [S4] | US Climate Data - Evant, Texas climate averages | https://www.usclimatedata.com/climate/evant/texas/united-states/ustx0439 | Average annual precipitation around 30.71 inches. |
| [S5] | TWDB - Trinity Aquifer | https://www.twdb.texas.gov/groundwater/aquifer/majors/trinity.asp | Trinity Aquifer description and units. |
| [S6] | Middle Trinity Groundwater Conservation District | https://www.middletrinitygcd.org/ | Groundwater district relevant if property is in Coryell County. |
| [S7] | Middle Trinity GCD - About Us | https://www.middletrinitygcd.org/about-us | District mission and activities. |
| [S8] | TWDB - Groundwater Conservation Districts | https://www.twdb.texas.gov/groundwater/conservation_districts/ | GCD identification resources. |
| [S9] | TSSWCB - Hamilton-Coryell SWCD #506 | https://tsswcb.texas.gov/swcds/506 | Local soil and water conservation district contact. |
| [S10] | Texas State Soil and Water Conservation Board | https://tsswcb.texas.gov/ | State agency role for agricultural/silvicultural nonpoint-source water pollution. |
| [S11] | USDA NRCS - Web Soil Survey | https://websoilsurvey.nrcs.usda.gov/ | Soil data for ranch planning and site screening. |
| [S12] | Texas Well Owner Network | https://twon.tamu.edu/ | Private well owner education and testing resources. |
| [S13] | Texas A&M AgriLife - Texas Well Owner Network program overview | https://agrilifeextension.tamu.edu/asset-local/texas-well-owner-network/ | Private well owner responsibility and training. |
| [S14] | NRCS - Web Soil Survey overview | https://www.nrcs.usda.gov/resources/data-and-reports/web-soil-survey | Official soil data and land-use decision support. |
| [S15] | TCEQ - Am I Regulated? Water Rights in Texas | https://www.tceq.texas.gov/permitting/water_rights/wr-permitting/wr_amiregulated.html | Surface water permission and exempt-use overview. |
| [S16] | Texas A&M AgriLife - A Pond to Call My Own: Understanding Water Law in Texas | https://extension.rwfm.tamu.edu/wp-content/uploads/sites/8/2013/09/A-Pond-to-Call-My-Own-Understanding-Water-Law-in-Texas.pdf | Educational overview of ponds, diffused surface water, and exemptions. |

# 28. First 30 Days Action Plan for Luke

This is the practical starting plan. The first 30 days should be about data, maps, measurements, and narrowing the design. Avoid major purchases until these are done.

| Timeframe | Work | Deliverable |
| --- | --- | --- |
| Week 1 | Create folder, read this packet, walk site, photograph house/gutters/tank site/well/pipe route, confirm county/parcel, request well documents. | Photo set, parcel/county confirmation, document request list. |
| Week 2 | Measure roof catchment and downspouts, measure rough elevations, map pipe route, inspect tank site, collect existing water-use assumptions. | Roof area table, elevation notes, preliminary site map. |
| Week 3 | Contact GCD/county/SWCD/NRCS as appropriate, order water tests, gather tank vendor foundation requirements, start 20k/30k/50k model. | Regulatory notes, water test plan, tank options, model draft. |
| Week 4 | Prepare concept alternatives for Ben: practical backup, serious household/ranch backup, full ranch water master plan. Identify red flags and contractor scopes. | Decision meeting packet and bid scope draft. |

## Before Luke asks contractors for prices

[ ] Roof area measured.

[ ] Tank site selected or at least narrowed to two options.

[ ] Elevation difference measured well enough for preliminary pump/conveyance design.

[ ] Potable vs non-potable direction selected.

[ ] Well documents requested or obtained.

[ ] County/GCD jurisdiction identified.

[ ] Tank size scenarios modeled.

[ ] Overflow route selected.

[ ] Foundation requirements requested from tank vendors.

[ ] Bid scopes written so quotes are comparable.

## Before Ben approves construction

[ ] Final scope selected.

[ ] Contractor bids compared apples-to-apples.

[ ] Foundation/pad detail approved by tank vendor or engineer.

[ ] Plumbing/backflow plan approved if any house connection exists.

[ ] Electrical plan approved by electrician.

[ ] Regulatory questions answered.

[ ] Water treatment plan defined if potable.

[ ] Maintenance owner assigned.

[ ] Contingency budget set.

[ ] Construction sequence and responsibilities documented.

# 29. Bottom-Line Guidance

The project should be approached with ambition and restraint at the same time. The ambition is right: a 500-acre Texas ranch should have a serious water plan. The restraint is also necessary: one 3,000 sq. ft. roof is not enough to solve every ranch water need. It can be a very good clean-water source, especially for backup, garden, and resilience, but it should be one layer in a broader plan.

Luke’s job is to convert the vision into measured facts, a water balance model, a site plan, and a staged budget. The right first win is not a giant tank. The right first win is a clear design that Ben can trust before spending serious money.